## About DTTM-BP
CIGRE DTTM Benchmarking platform
Prepared by CIGRE working group A2.60
More information on the GitLab project:
https://gitlab.com/cigrea2.60/cigre-dttm-benchmarking-platform
Contacts:
Tim GRADNIK (tim.gradnik@eimv.si)
Remi DESQUIENS (remi.desquiens@edf.fr)
License information
Copyright 2024 Tim GRADNIK and the CIGRE working group A2.60. This program is free software: you can redistribute it and/or modify it under the terms of the GNU General Public License as published by the Free Software Foundation, either version 3 of the License, or (at your option) any later version.
This program is distributed in the hope that it will be useful, but WITHOUT ANY WARRANTY; without even the implied warranty of MERCHANTABILITY or FITNESS FOR A PARTICULAR PURPOSE. See the GNU General Public License for more details: https://www.gnu.org/licenses/gpl-3.0.html
Redistribution and use in source and binary forms, with or without modification, are permitted provided that the following conditions are met:
1. Redistributions of source code must retain the above copyright notice, this list of conditions and the following disclaimer.
2. Redistributions in binary form must reproduce the above copyright notice, this list of conditions and the following disclaimer in the documentation and/or other materials provided with the distribution.
3. Neither the name of the copyright holder nor the names of its contributors may be used to endorse or promote products derived from this software without specific prior written permission. Copyright holder contact: Tim GRADNIK(tim.gradnik@eimv.si) and DESQUIENS Remi (remi.desquiens@edf.fr).
THIS SOFTWARE IS PROVIDED BY THE COPYRIGHT HOLDERS AND CONTRIBUTORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE COPYRIGHT HOLDER OR CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

## TTS description
Parameters for ONAN/ONAFx transformers
Component | Name | Symbol | Unit | Values |  |  |  | Remark to parameter
Systems | Name of electrical system | snam | - | HV | LV | - | -
| Nominal voltage (at nominal tap position) | Unom | kV | 225 | 26.4 | - | - | phase-to-phase
| Nominal power (at AFmax) | Snom | MVA | 66 | 66 | - | -
| Connection | conn | - | star | delta | - | - | use "star" or "delta"
| Type of regulation | reg_typ | - | Boost/Buck | none | - | - | use "none", "tapped", "Boost wind.", "Boost/Buck wind." or "Fine/Coarse wind."
| Voltage at minus position | min-tap | kV | 202.5 | - | - | - | for TTSa: only nominal tap is modeled, Tap Position is missing in time series
| Voltage at nominal position | nom-tap | kV | 225 | - | - | -
| Voltage at plus position | plus-tap | kV | 247.5 | - | - | -
| Percentage per regulation step | reg-step | % | 1.25 | - | - | -
Tank | Length of tank | LK | mm | 4520
| Width of tank | WK | mm | 2560
| Height of tank | HK | mm | 3369
| Oil volume (20 °C) in tank | Voil,tank | m³ | 32.5864 |  |  |  | for TTSa: estimated with 80 % of total oil. Total oil according to nameplate is 8960 imperial gallon. So it's 40.7 m3, 80% are 32.59 m3.
| Position of oil inlet from radiator | dinlet | mm | 800 |  |  |  | distance from tank bottom
| Insulation fluid | fluid | - | mineral |  |  |  | use "mineral", "nat. ester" or "synt. ester"
| Distance between upper yoke and tank | Ayoke,cover | mm | 410
| Eddy Losses outside the winding (nominal tap) | Ps | kW | 59.9
Core | Core diameter | Ds | mm | 587
| Heigth of core limb | HF | mm | 1690 |  |  |  | Is this the heigth of the window? 1699 mm is the size of the window (see picture)
| Main yoke height | Bj | mm | 587
| Limb center distance | Ecenter | mm | 1272
| Total core mass | GFE | kg | 22500 |  |  |  | The mass of the core and coils is 33203 kg (nameplate). OK. Total of core and winding mass shown with lines 27 and 42.
| Number of wounded limbs | Nlimb | - | 3
| Core losses at nominal voltage | Pc | kW | 50.3
| Temperature gradient to core surface | gsur | K |  |  |  |  | optional input
| Temperature gradient to inner package | gpac | K |  |  |  |  | optional input
| Longitudinal oil temperature rise in oil ducts | Dc | K |  |  |  |  | optional input
P_C
Windings | Name of winding | wnam | - | LV | HV | - | -
| Inner diameter | Di | mm | 650 | 960 | - | -
| Outer diameter | Do | mm | 752 | 1122 | - | -
| Height | Hw | mm | 1499 | 1499 | - | -
| Summarized heigth of spacers | Hspac | mm | 326 | 392 | - | - | Winding_heigth - (number of disc * heigth of disc with paper insulation)
| Summarized width of all axial ducts | Wduct | mm | 14.82 | 19 | - | - | Inner axial duct + outer axial duct (dimensions in the cells)
| Upper yoke clearance | Ao | mm | 113 | 113 | - | -
| Lower yoke clearance | Au | mm | 78 | 78 | - | -
| Solid winding mass (all wounded limbs) | msolid | kg | 3187 | 7516 | - | -
| Paper insulation mass (all wounded limbs) | mpaper | kg |  |  | - | - | optional input
| Conductor Material | wmat | - | Cu | Cu | - | - | use "Cu" or "Al"
| Ohmic resistance per phase (75 °C) | Rohm | Ω | 0.06262 | 2.3343 | - | -
| Eddy Losses (75 °C) in plus tap position (all wounded limbs) | Peddy,plus,tap | kW |  |  | - | -
| Eddy Losses (75 °C) in nominal tap position (all wounded limbs) | Peddy,nom,tap | kW | 23.03 | 10.16 | - | -
| Eddy losses (75 °C) in minus tap position (all wounded limbs) | Peddy,minus,tab | kW |  |  | - | -
| Average temperature gradient (nominal power, nominal tap) | gw,av | K | 27.75 | 13.05 | - | - | based on inner winding oil temperature, for TTSa: estimated from heat run data
| Hotspot temperature gradient (nominal power, nominal tap) | gw,hs | K |  |  | - | - | based on inner winding oil temperature, for TTSa: data about hotspot rise not available
| Longitudinal oil temperature rise in oil ducts (nominal power, nominal tap) | Dw | K |  |  | - | -
| Average winding temperatue rise (nominal power, nominal tap) | Δθaw | K | 61.6 | 46.9 | - | - | parameter ideally from heat run test
| Hotspot winding temperature rise (nominal power, nominal tap) | Δθhs | K |  |  | - | - | parameter ideally from heat run test, for TTSa: data about hotspot rise not available
| Exponent over losses for average winding gradient | xp,av | - |  |  | - | - | optional input
| Exponent over losses for hotspot winding gradient | xp,hs | - |  |  | - | - | optional input
-
Cooler | AN loading factor | KAN | - | 0.60606 |  |  |  | AN/AFmax loading
| Name of cooling stages | stage | - | AN | AF1 | AF2 | -
| Number of active fans (or groups) | nfan | - | 0 | 3 | 6 | - | There are 2 cooling units (block of radiators) with 6 fans each.
| Average oil temperature rise at radiator | Δθom | K | 40.7 |  | 33.85 | - | parameter from heat run test
| Top liquid temperature rise at radiator | Δθo | K | 53.3 |  | 51.2 | - | parameter from heat run test
| Distance from tank bottom to cooler top | Hcool,top | mm | 3086
| Radiator height | dcooler | mm | 2286
| Oil volume (20 °C) in radiator | Voil,cooler | m³ | 8.1466 |  |  |  | for TTSa: estimated with 20 % of total oil
HR test | 66 MVA, 225/26.4 kV, ONAN/ONAF)
RI2 losses at 1 pu, tap 9 (neutral) and 75°C = 331406 W
Stray losses at 1 pu, tap 9 (neutral) and 75°C = 93070 W (Eddy+Stray actually)
Core losses = 50300 W
R=8.44
Weight of core and coil = 73200 lbs = 33203 kg
Weight of tanks and fittings = 54200 lbs = 24585 kg
Oil type = mineral oil
Volume of oil = 8960 gallons imperial = 40733 litres
Weight of oil = 76600 lbs = 34745 kg
The heat-run test results indicate a winding temperature rise of 61.6°C. The ambient temperature, top oil temperature and bottom oil temperature at the end of the heat run test were respectively 30.2°C, 81.4°C and 46.7°C.
WTI and cooling thermostat settings
HGr(HV) = 10.7 °C
HGr(LV) = 25.4 °C
ONAF2 turn on: 75°C
turn off: 65 °C
ONAF1 turn on: 65 °C
turn off: 55 °C
The "hot-spot" is the temperaturemeasured using a FO probe in a spacer between disks 75 and 76 of phaseB. The ambient temperature is measured using a temperature sensor near the transformer. The top-oil is measured using a RTD located in athermo-well under the tank cover. The bottom oil is measured using a FOprobe near the oil entrance at the bottom of the winding. The HV and LVcurrents are in Ampere. Rated HV and LV currents are 169 A and 1443 A.
Liquid | Temperature (deg C) | Temperature (deg K) | Density (kg/m^3) | Specific heat capacity (J/kg*K) | Thermal conductivity (W/m*K) | Kinematic viscosity (m^2/s) | Kinematic viscosity (m^2/s) |  | Dynamic viscosity (Pa*s)
| -20 | 253.15 | 890.4 | 1600 | 0.13016 | 0.00010523 | 105.2302 |  | 0
| -10 | 263.15 | 883.7 | 1600 | 0.12725 | 4.7177e-05 | 47.1774 |  | 0
| 0 | 273.15 | 876.95 | 1610 | 0.12442 | 2.4385e-05 | 24.3845 |  | 0
| 10 | 283.15 | 870.2 | 1630 | 0.12239 | 1.4191e-05 | 14.1906 |  | 0
| 20 | 293.15 | 863.3 | 1640 | 0.12021 | 9.1177e-06 | 9.1177 |  | 0
| 30 | 303.15 | 856.6 | 1660 | 0.11854 | 6.2819e-06 | 6.2819 |  | 0
| 40 | 313.15 | 849.95 | 1685 | 0.11693 | 4.6012e-06 | 4.6012 |  | 0
| 50 | 323.15 | 843.35 | 1710 | 0.11533 | 3.5402e-06 | 3.5402 |  | 0
| 60 | 333.15 | 836.7 | 1740 | 0.11397 | 2.8352e-06 | 2.8352 |  | 0
| 70 | 343.15 | 830.15 | 1765 | 0.11266 | 2.346e-06 | 2.346 |  | 0
| 80 | 353.15 | 823.55 | 1800 | 0.11153 | 1.9935e-06 | 1.9935 |  | 0
| 90 | 363.15 | 817 | 1830 | 0.11039 | 1.7315e-06 | 1.7315 |  | 0
| 100 | 373.15 | 810.2 | 1865 | 0.11 | 1.5315e-06 | 1.5315 |  | 0

## TTS parameters
input/output | parameter type | group | longname | shortname | value | unit | to be distributed to proprietary DTTM | models | remarks
output | timeseries | Tank | Bottom liquid temperature | t_bl |  | °C
output | timeseries | Tank | Top liquid temperature | t_tl |  | °C
output | timeseries | Windings | Hot-spot temperature | t_hs |  | °C
output | timeseries | Windings | Winding temp. indicator | t_wti |  | °C
input | timeseries | Operation | Load factor | load |  | pu
input | timeseries | Operation | Ambient temperature | t_amb |  | °C
input | timeseries | Cooler | Fan group 1 status | fangr1 |  | 1/0
input | timeseries | Cooler | Fan group 2 status | fangr2 |  | 1/0
input | timeseries | Cooler | Fan group 3 status | fangr3 |  | 1/0
input | timeseries | Cooler | Cooling stage | cooling_stage |  | 1/0
input | timeseries | Tap changer | Tap position | tap_pos |  | int
input | timeseries | Operation | Sun irradiation | irrad |  | W/m2
input | timeseries | Operation | Wind speed | wind_speed |  | m/s
input | timeseries | Operation | Precipation rate | prec_rate |  | mm/h
input | from_standard | Cooler | top liquid nonlinearity factor | x_iec | 0.8 | - | no | IEC60076_top_liquid,IEC60076_VCS1_top_liquid,IEC60076_VCS1amb_hotspot,IEC60076_VCS2_top_liquid,IEC60076_VTP1_top_liquid,IEC60354_hotspot
input | from_standard | Windings | winding nonlinearity factor | y_iec | 1.3 | - | no | IEC60076_hotspot,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot,IEC60076_VTP1_hotspot,IEC60354_hotspot,ASNZS60076_hotspot
input | from_standard | Cooler | top-liquid time constant correction factor | k11 | 1 | - | no | IEC60076_top_liquid,IEC60076_VCS1_top_liquid,IEC60076_VCS1amb_hotspot,IEC60076_VCS2_top_liquid,IEC60076_VTP1_top_liquid
input | from_standard | Windings | hotspot thermal overshoot factor 1 | k21 | 1 | - | no | IEC60076_hotspot,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot,IEC60076_VTP1_hotspot,ASNZS60076_hotspot
input | from_standard | Windings | hotspot thermal overshoot factor 2 | k22 | 1 | - | no | IEC60076_hotspot,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot,IEC60076_VTP1_hotspot,ASNZS60076_hotspot
input | constant | Windings | Rated Load to no-load losses ratio | R | 8.44 | - | no | IEC60076_top_liquid,IEC60076_VCS1_top_liquid,IEC60076_VCS1amb_hotspot,IEC60076_VCS2_top_liquid,IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,IEC60354_hotspot
input | fitted | Cooler | Rated cooling stage 2 TL temp rise | T_tl_2_iec | 51.3 | K | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1amb_hotspot
input | fitted | Cooler | Rated cooling stage 1 TL temp rise | T_tl_1_iec | 69.5 | K | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1amb_hotspot
input | fitted | Cooler | Rated cooling stage 0 TL temp rise | T_tl_0_iec | 98.3 | K | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1amb_hotspot
input | constant | Cooler | Rated BL temp rise | T_bl_iec | 16.5 | K | no | IEC60354_hotspot
input | constant | Cooler | Rated ML temp rise | T_ml_iec | 33.8 | K | no | IEC60354_hotspot
input | constant | Cooler | Rated TL temp rise | T_tl_iec | 51.2 | K | no | IEC60076_top_liquid,IEC60076_VCS2_top_liquid,IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot
input | fitted | Cooler | Rated cooling stage 2 time constant | Tau_tl_2_iec | 150 | min | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot
input | fitted | Cooler | Rated cooling stage 1 time constant | Tau_tl_1_iec | 210 | min | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot
input | fitted | Cooler | Rated cooling stage 0 time constant | Tau_tl_0_iec | 210 | min | no | IEC60076_VCS1_top_liquid,IEC60076_evolution_top_liquid,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot
input | from_standard | Cooler | Rated time constant | Tau_tl_iec | 150 | min | no | IEC60076_top_liquid,IEC60076_hotspot,IEC60076_VCS2_top_liquid,IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,ASNZS60076_hotspot
input | from_standard | Cooler | Rated time constant | Tau_bl_iec | 150 | min | no | IEC60354_hotspot
input | from_standard | Cooler | Rated time constant | Tau_w_iec | 10 | min | no | IEC60354_hotspot
input | constant | Windings | Rated hot-spot gradient | T_hgr_iec | 25.4 | K | no | IEC60076_hotspot,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot,IEC60354_hotspot,ASNZS60076_hotspot | 25,4 LV 10,7 HV
input | from_standard | Windings | Hot-spot time constant | Tau_hgr_iec | 7 | min | no | IEC60076_hotspot,IEC60076_VCS1tl_hotspot,IEC60076_VCS1amb_hotspot,IEC60076_VTP1_hotspot,ASNZS60076_hotspot
input | constant | Cooler | Rated power cooling stage 0 | S_nom_0_iec | 40 | MVA | no | IEC60076_VCS2_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid
input | constant | Cooler | Rated power cooling stage 1 | S_nom_1_iec | 53 | MVA | no | IEC60076_VCS2_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid
input | constant | Cooler | OTI cooling control | C_OTI_act |  | boolean | yes
input | constant | Windings | WTI cooling control | C_WTI_act |  | boolean | yes
input | constant | Cooler | load-based cooling control | C_load_act |  | boolean | yes
input | constant | Windings | C2 WTI turn on temperature | C2WTI_on | 75 | °C | yes
input | constant | Windings | C2 WTI turn off temperature | C2WTI_off | 65 | °C | yes
input | constant | Windings | C1 WTI turn on temperature | C1WTI_on | 65 | °C | yes
input | constant | Windings | C1 WTI turn off temperature | C1WTI_off | 55 | °C | yes
input | constant | Cooler | C2 OTI turn on temperature | C2OTI_on |  | °C | yes
input | constant | Cooler | C2 OTI turn off temperature | C2OTI_off |  | °C | yes
input | constant | Cooler | C1 OTI turn on temperature | C1OTI_on |  | °C | yes
input | constant | Cooler | C1 OTI turn off temperature | C1OTI_off |  | °C | yes
input | constant | Cooler | C2 load factor turn on temperature | C2load_on |  | °C | yes
input | constant | Cooler | C2 load factor off temperature | C2load_off |  | °C | yes
input | constant | Cooler | C1 load factor turn on temperature | C1load_on |  | °C | yes
input | constant | Cooler | C1 load factor turn off temperature | C1load_off |  | °C | yes
input | constant | Cooler | Cooling stage 0 fan number | fanstage0 | 0 | int | yes
input | constant | Cooler | Cooling stage 1 fan number | fanstage1 | 1 | int | yes
input | constant | Cooler | Cooling stage 2 fan number | fanstage2 | 2 | int | yes
input | data_array | Systems | Nominal voltage (at nominal tap) | U_nom |  | kV | yes |  | phase-to-phase
input | data_array | Systems | Nominal power | S_nom | 66 | MVA | yes | IEC60076_VCS2_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid
input | data_array | Systems | Connection | conn |  | - | yes |  | star, delta
input | data_array | Systems | Type of regulation | reg_typ |  | - | yes |  | none, tapped, boost wind., boost/buck wind., fine/coarse wind.
input | data_array | Systems | Identifier of minus position | min_tap |  | - | yes
input | data_array | Systems | Identifier of nominal position | nom_tap |  | - | yes
input | data_array | Systems | Identifier of plus position | plus_tap |  | - | yes
input | data_array | Systems | Percentage per regulation step | reg_step |  | % | yes
input | constant | Tank | Length of tank | L_k |  | mm | yes
input | constant | Tank | Width of tank | W_k |  | mm | yes
input | constant | Tank | Height of tank | H_k |  | mm | yes
input | constant | Tank | liquid volume (20 °C) in tank | V_oil_tank |  | m³ | yes
input | constant | Tank | Position of liquid inlet from radiator | d_inlet |  | mm | yes |  | distance from tank bottom
input | constant | Tank | Insulation fluid | fluid |  | - | yes |  | mineral, nat. ester, syt. ester
input | constant | Tank | Distance between upper yoke and tank | A_yoke_cover |  | mm | yes
input | constant | Tank | Eddy Losses outside the winding (nominal tap) | P_S |  | kW | yes
input | constant | Core | Core diameter | D_S |  | mm | yes
input | constant | Core | Heigth of core limb | H_F |  | mm | yes
input | constant | Core | Main yoke height | B_J |  | mm | yes
input | constant | Core | Limb center distance | E_center |  | mm | yes
input | constant | Core | Total core mass | G_FE |  | kg | yes
input | constant | Core | Number of wounded limbs | N_limb |  | - | yes
input | constant | Core | Core losses at nominal voltage | P_C |  | kW | yes
input | constant | Core | Temperature gradient to core surface | g_c_sur |  | K | yes |  | optional input
input | constant | Core | Temperature gradient to inner package | g_c_pac |  | K | yes |  | optional input
input | constant | Core | Longitudinal liquid temperature rise in liquid ducts | D_C |  | K | yes |  | optional input
input | data_array | Windings | Name of winding | wnam |  | - | yes
input | data_array | Windings | Inner diameter | D_i |  | mm | yes
input | data_array | Windings | Outer diameter | D_o |  | mm | yes
input | data_array | Windings | Height | H_w |  | mm | yes
input | data_array | Windings | Summarized heigth of spacers | H_spac |  | mm | yes
input | data_array | Windings | Summarized width of all axial ducts | W_duct |  | mm | yes
input | data_array | Windings | Upper yoke clearance | A_o |  | mm | yes
input | data_array | Windings | Lower yoke clearance | A_u |  | mm | yes
input | data_array | Windings | Solid winding mass (all wounded limbs) | m_solid |  | kg | yes
input | data_array | Windings | Paper insulation mass (all wounded limbs) | m_paper |  | kg | yes |  | optional input
input | data_array | Windings | Conductor Material | wmat |  | - | yes |  | Cu, Al
input | data_array | Windings | Ohmic resistance per phase (75 °C) | R_ohm |  | Ω | yes
input | data_array | Windings | Eddy Losses (75 °C) in plus tap position (all wounded limbs) | P_eddy_plus |  | kW | yes
input | data_array | Windings | Eddy Losses (75 °C) in nominal tap position (all wounded limbs) | P_eddy_nom |  | kW | yes
input | data_array | Windings | Eddy losses (75 °C) in minus tap position (all wounded limbs) | P_eddy_minus |  | kW | yes
input | data_array | Windings | Average temperature gradient (nominal power, nominal tap) | g_w_av |  | K | yes
input | data_array | Windings | Hotspot temperature gradient (nominal power, nominal tap) | g_w_hs |  | K | yes
input | data_array | Windings | Longitudinal liquid temperature rise in liquid ducts (nominal power, nominal tap) | D_w |  | K | yes
input | data_array | Windings | Hotspot winding temperature rise (nominal power, nominal tap) | dTheta_hs |  | K | yes |  | parameter ideally from heat run test
input | data_array | Windings | Exponent over losses for average winding gradient | x_p_av |  | - | yes |  | optional input
input | data_array | Windings | Exponent over losses for hotspot winding gradient | x_p_hs |  | - | yes |  | optional input
input | constant | Cooler | AN loading factor | K_AN |  | - | yes |  | AN power/AFmax power
input | data_array | Cooler | Name of cooling stages | stage |  | - | yes
input | data_array | Cooler | Number of active fans (or groups) | n_fan |  | - | yes
input | data_array | Cooler | Average liquid temperature rise at radiator | dTheta_om |  | K | yes |  | parameter ideally from heat run test
input | data_array | Cooler | Top liquid temperature rise at radiator | dTheta_o |  | K | yes |  | parameter ideally from heat run test
input | constant | Cooler | Distance from tank bottom to cooler top | H_cool_top |  | mm | yes
input | constant | Cooler | Radiator height | d_cool |  | mm | yes
input | constant | Cooler | liquid volume (20 °C) in radiator | V_oil_cool |  | m³ | yes
input | constant | Windings | Paper type | typePaper | not-tup |  | yes | IEEEC57_91_G_from_IEEE_top_liquid | "tup" or "not-tup"
input | constant | Windings | Ageing parameters | ageingParameters | Free from air and 0.5 % moisture |  | yes |  | "Standard (no air and moisture consideration)", "Free from air and 0.5 % moisture", "Free from air and 1.5 % moisture", "Free from air and 3.5 % moisture", "With air and 0.5 % moisture"
input | constant | Windings | Winding I2R loss at rated load | P_w | 331406 | W | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Windings | Eddy loss of windings at rated load | P_e | 46535 | W | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Windings | Stray losses at rated load | P_s | 46535 | W | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Core | Core (no-load) loss | P_c_r | 50300 | W | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Average winding temperature rise over ambient at rated load tested | Dt_w_r | 61.6 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Winding hottest-spot temperature rise over ambient at rated load | Dt_h_r | 76.6 | K | no | IEEEC57_91_G_hotspot,IEEEC57_91_G_from_IEEE_top_liquid | 51.2+25.4
input | constant | Cooler | Top fluid temperature rise over ambient in tank and radiator at rated load | Dt_to_r | 51.2 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Bottom fluid temperature rise over ambient at rated load | Dt_bo_r | 16.5 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Average winding temperature rise over ambient at rated load tested | Dt_w_r_ONAN | 61.6 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Winding hottest-spot temperature rise over ambient at rated load | Dt_h_r_ONAN | 76.6 | K | no | IEEEC57_91_G_hotspot | 51.2+25.4
input | constant | Cooler | Top fluid temperature rise over ambient in tank and radiator at rated load | Dt_to_r_ONAN | 51.2 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Bottom fluid temperature rise over ambient at rated load | Dt_bo_r_ONAN | 16.5 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Average winding temperature rise over ambient at rated load tested | Dt_w_r_ONAF1 | 61.6 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Winding hottest-spot temperature rise over ambient at rated load | Dt_h_r_ONAF1 | 76.6 | K | no | IEEEC57_91_G_hotspot | 51.2+25.4
input | constant | Cooler | Top fluid temperature rise over ambient in tank and radiator at rated load | Dt_to_r_ONAF1 | 51.2 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Bottom fluid temperature rise over ambient at rated load | Dt_bo_r_ONAF1 | 16.5 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Average winding temperature rise over ambient at rated load tested | Dt_w_r_ONAF2 | 61.6 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Winding hottest-spot temperature rise over ambient at rated load | Dt_h_r_ONAF2 | 76.6 | K | no | IEEEC57_91_G_hotspot | 51.2+25.4
input | constant | Cooler | Top fluid temperature rise over ambient in tank and radiator at rated load | Dt_to_r_ONAF2 | 51.2 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Bottom fluid temperature rise over ambient at rated load | Dt_bo_r_ONAF2 | 16.5 | K | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Rated ambient at kVA base for load cycle | t_a_r | 30.2 | °C | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Windings | Winding material | w_material | copper |  | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot | "copper" or "aluminium"
input | constant | Windings | Eddy loss at winding hot spot location | E_hs | 0 | per unit of I2R loss | no | IEEEC57_91_G_hotspot,IEEEC57_91_G_from_IEEE_top_liquid | 0 if unknown
input | constant | Windings | Winding time constant | tau_w | 5 | min | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot | 5 min suggested
input | constant | Windings | Per unit of winding height to hot spot location | H_hs | 1 |  | no | IEEEC57_91_G_hotspot,IEEEC57_91_G_from_IEEE_top_liquid | 1 if unknown
input | constant | Core | Core and coil (untanking) weight | M_cc | 73200 | lb | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Tank | Mass of tank | M_tank | 54200 | lb | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Cooler | Liquid_material | l_material | oil |  | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_hotspot | "oil", "silicone" or "HTHC"
input | constant | Cooler | Liquid_material | l_material | mineral oil |  | no | IEEEC57_91_G_from_IEEE_top_liquid | "mineral oil", "silicone", "hthc", "fr3"
input | constant | Cooler | Mass of fluid | M_oil | 76600 | lb | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot
input | constant | Core | Type of core excitation | excitation | normal |  | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot | "normal" or "over"
input | constant | Core | Core loss when overexcitation occurs | P_c_oe | 50300 | W | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot | no data
input | constant | Cooler | Cooling mode | cooling_mode | ONAF |  | no | IEEEC57_91_G_top_liquid,IEEEC57_91_G_from_IEEE_top_liquid,IEEEC57_91_G_hotspot | "ONAN", "ONAF", "OFAF" or "ODAF"
input | constant | Cooler | Water content in paper | WCP | 0 | % | no | IEEEC57_91_G_from_IEEE_top_liquid
input | constant | Windings | Top oil time constant | Tau_tl_r | 150 | min | no | DSusa_top_liquid
input | constant | Windings | Winding time constant | Tau_w_r | 5 | min | no | DSusa_hotspot
input | constant | Windings | Ratio of load losses at rated current to no-load losses | R | 8.44 |  | no | DSusa_top_liquid
input | constant | Windings | DC loss per unit value | P_dc_pu | 0.78074 |  | no | DSusa_top_liquid,DSusa_hotspot
input | constant | Windings | Additional loss (i.e., equal to the sum of eddy and stray losses) per unit value | P_a_pu | 0.21926 |  | no | DSusa_top_liquid
input | constant | Windings | Eddy losses per unit value | P_e_pu | 0.10963 |  | no | DSusa_hotspot
input | constant | Windings | Winding material | w_material | copper |  | no | DSusa_top_liquid,DSusa_hotspot,IEC60076_evolution_top_liquid | "copper" or "aluminium"
input | constant | Cooler | Liquid_material | l_material | oil |  | no | DSusa_top_liquid,DSusa_hotspot,IEC60076_evolution_top_liquid | "oil" or "silicone"
input | constant | Cooler | Cooling mode | cooling_mode | ONAF |  | no | DSusa_top_liquid,DSusa_hotspot,IEC60076_evolution_top_liquid | "ONAN", "ONAF", "OFAF"
input | constant | Cooler | Rated ambient | t_a_r | 30.2 | °C | no | DSusa_top_liquid,DSusa_hotspot,IEC60076_evolution_top_liquid
input | constant | Cooler | Rated top-oil temperature rise over ambient temperature | TR_tl_r | 51.2 | K | no | DSusa_top_liquid,DSusa_hotspot
input | constant | Cooler | Rated hot-spot temperature rise over top-oil temperature | TR_hstl_r | 18.8 | K | no | DSusa_hotspot
input | constant | Tap changer | Rated tap position | tap_pos_r | 9 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,IEC60076_evolution_top_liquid
input | constant | Tap changer | Minus tap position | tap_pos_minus | 1 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,IEC60076_evolution_top_liquid
input | constant | Tap changer | Plus tap position | tap_pos_plus | 17 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,IEC60076_evolution_top_liquid
input | constant | Windings | Minus tap Load to no-load losses ratio | R_minus | 7.7964 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot
input | constant | Windings | Plus tap Load to no-load losses ratio | R_plus | 7.7964 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot | no data
input | constant | Windings | Rated tap +1 Load to no-load losses ratio | R_rp1 | 8.44 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot | no data
input | constant | Windings | Temperature rise test tap Load to no-load losses ratio | R_trt | 8.44 |  | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot
input | from_standard | Cooler | top liquid nonlinearity factor from 60076-2 | x_iec_76_2 | 0.8 | - | no | IEC60076_VTP1_top_liquid,IEC60076_VTP1_hotspot,IEC60076_evolution_top_liquid
input | from_standard | Windings | winding nonlinearity factor from 60076-2 | y_iec_76_2 | 1.6 | - | no | IEC60076_VTP1_hotspot
input | from_standard | Windings | hotspot nonlinearity factor from 60076-2 | z_iec_76_2 | 1.6 | - | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 1 | Ir_tap_1 | 153.9601 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 2 | Ir_tap_2 | 155.7294 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 3 | Ir_tap_3 | 157.5405 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 4 | Ir_tap_4 | 159.3936 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 5 | Ir_tap_5 | 161.2915 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 6 | Ir_tap_6 | 163.2344 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 7 | Ir_tap_7 | 165.2254 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 8 | Ir_tap_8 | 167.2649 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 9 | Ir_tap_9 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 10 | Ir_tap_10 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 11 | Ir_tap_11 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 12 | Ir_tap_12 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 13 | Ir_tap_13 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 14 | Ir_tap_14 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 15 | Ir_tap_15 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 16 | Ir_tap_16 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Tap changer | Rated HV current tap 17 | Ir_tap_17 | 169.3561 | A | no | IEC60076_VTP1_hotspot
input | constant | Windings | Average winding gradient | g_w | 27.75 | K | no | IEC60076_VTP1_hotspot | 27,75 LV 13,05 HV
input | constant | Windings | Hot-spot winding gradient | g_hs | 25.4 | K | no | IEC60076_VTP1_hotspot | 25,4 LV 10,7 HV
input | constant | Windings | Hotspot on the tapped winding | loc_hs_tap | no |  | no | IEC60076_VTP1_hotspot | "yes" or "no"
input | constant | Cooler | Liquid VFT A parameter | VFT_A | 0.1351 |  | no | IEC60076_evolution_top_liquid
input | constant | Cooler | Liquid VFT B parameter | VFT_B | 458.6 |  | no | IEC60076_evolution_top_liquid
input | constant | Cooler | Liquid VFT C parameter | VFT_C | 184.1 |  | no | IEC60076_evolution_top_liquid
input | constant | Windings | DC loss tap minus | P_dc_minus | 308267 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | DC loss tap rated | P_dc_r | 331372 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | DC loss tap rated plus 1 | P_dc_rp1 | 327330 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | DC loss tap plus | P_dc_plus | 308267 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | DC loss tap Temperature Rise Test | P_dc_trt | 331372 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | Additional loss tap minus | P_a_minus | 83894 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | Additional loss tap rated | P_a_r | 93128 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | Additional loss tap rated plus 1 | P_a_rp1 | 93128 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | Additional loss tap plus | P_a_plus | 83894 | W | no | IEC60076_evolution_top_liquid
input | constant | Windings | Additional loss tap Temperature Rise Test | P_a_trt | 93128 | W | no | IEC60076_evolution_top_liquid
input | constant | Core | No-load loss | P_0 | 50300 | W | no | IEC60076_evolution_top_liquid

## fields
parameter type | Grouping of parameters | input/output | to be distributed to proprietary DTTM
constant | Cooler | input | yes
data_array | Core | output | no
fitted | Operation
from_standard | Systems
timeseries | Tank
Tap changer
Windings